KGS FS452(가스도매사업 정압기(지) 및 밸브기지의 시설·기술·검사 기준) 개정안 항목별 개정사유

현   행

개  정  (안)

개정사유

표 2.5.4.1.4② 설계계수

지역 구분	지 역 분 류 기 준	설계 계수(F)
가	지상 4층 이상의 건축물 밀집지역 또는 교통량이 많은 지역으로서 지하에 여러 종류의 공익시설물(전기·가스·수도배관 시설물)이 있는 지역	0.4
나	□가□에 해당하지 아니하는 지역으로서 밀도지수가 46 이상인 지역	0.5
다	□가□에 해당하지 아니하는 지역으로서 밀도지수가 46 미만인 지역	0.6
[비고] □밀도지수□란 배관의 임의지점에서 1.6 ㎞, 배관중심으로부터 좌우로 각각 폭 0.2 ㎞의 범위를 임의로 설정하였을 경우 그 구역 안에 있는 가옥수(아파트 등 복합건축물의 가옥숫자는 건축물 안의 독립된 가구수로 한다)를 말한다.

표 2.5.4.1.4② ---------

-- --	-------	---- ----
가	(가) ~ (다) <현행과 같음>
나
다
[비고] --------- 임의의 지점에서 길이방향으로 1.6 ㎞, 배관 중심으로부터 좌우로 각각 폭 0.2 ㎞의 범위에 있는 --- ----------------------------------- -----------------------.

ㅇ 밀도지수 정의의 명확화

ㅇ ASME 31.8 기준

- 배관 중심으로부터 0.4km, 배관 길이방향으로 임의지점에서 1.6km 구간의 독립된 가옥수로 밀도지수를 산정함.

840.2 Buildings Intended for Human Occupancy

840.2.1 General

(a) To determine the number of buildings intended for human occupancy for an onshore pipeline, lay out a zone 1⁄4-mi (0.4-km) wide along the route of the pipeline with the pipeline on the centerline of this zone, and divide the pipeline into random sections 1 mi (1.6 km) in length such that the individual lengths will include the maximum number of buildings intended for human occupancy. Count the number of buildings intended for human occupancy within each 1-mi (1.6-km) zone. For this purpose, each separate dwelling unit in a multiple dwelling unit building is to be counted as a separate building intended for human occupancy.